SECTION 28 0528.33

Device Boxes for Electronic Safety and Security

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

PART 1 – GENERAL

1.01	SUMMARY

- Section includes boxes and conduits related to the installation of telecommunications      cable supporting voice, data, sound reinforcement, and video (A/V) systems

- Related Sections:

1.   Section 26 0533 - Raceways and Boxes for Electrical Systems

2.   Section 27 0528.29 - Hangers and Supports for Communications Systems

3.   Section 27 0528.36 - Cable Trays for Communications Systems

4.   Section 27 0528.39 - Surface Raceways for Communications Systems

5.   Section 27 1300 - Communications Backbone Cabling

6.   Section 27 1500 - Communications Horizontal Cabling

1.02	REFERENCES

A.	Underwriters Laboratories, Inc. (UL)

B.	National Fire Protection Association (NFPA)

C.	National Electrical Code (NEC)

D.	Building Industry Consulting Service International (Bicsi)

1.03	SUBMITTALS

A.	Comply with Section 00 43 93 – Bid Submittal Checklist

B.	Product Data:

1. 	Submit manufacturer’s descriptive literature and product specifications for each product.

2. 	Manufacturer’s product drawings.

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship.

B.	Furnished products shall be listed or classified by third party agencies as suitable for the intended purpose.

1.  Underwriters Laboratories, Inc. (UL)

C. 	Manufacturer shall be ISO 9001 certified.

  - WARRANTY

- Product is warranted free of defects in material and workmanship.

- Product is warranted to perform the intended function within design limits.

PART 2 – PRODUCTS

2.01	GENERAL

- Materials shall consist of appliance/device boxes, fittings, enclosures, and other raceway

incidentals and accessories as required for electronic safety and security circuits and appliance/devices.

- Boxes and covers shall be third party certified to:

  - UL 514A  “Metallic Outlet Boxes”

  - UL 514D  “Cover Plates for Flush-Mounted Wiring Devices”

2.02	MANUFACTURERS

- Acceptable Manufacturers:

Eaton’s Crouse-Hinds Business

1201 Wolf Street

Syracuse, NY 13208

(866) 764-5454

www.crouse-hinds.com

Product: Crouse-Hinds Metallic Boxes, Covers & Accessories

  - MATERIALS

- Low Voltage Boxes:

  - All 5 inch Square Boxes shall have the following characteristics:

    - Outside Dimensions:

      - 5 in (127 mm) Width

      - 5 in (127 mm) Height

      - 2 7/8 in (73.025) Depth

      - 67 cubic inch Volume (1097.93 CM3)

    - Materials:

- Galvanized Steel, 0.0625 inch thickness (minimum)

    - Construction:

      - Welded at 14 points (minimum)

    - Grounding

      - 1 #10-32 threaded hole for ground screw

    - Mounting/Attachment Features:

      - For Cut-In Mounting: 2 holes (0.16 in (4.0 mm) diameter) on each side

      - For Back Support Mounting: 2 holes (0.266 in (6.75 mm)) on back

      - For Box Support Bracket Installation: 4 tabs with tapped holes (8-32) on front of box with a distance of 2 ¾ in (69.85 mm) between both sets of plate mounting screws.

    - Testing / Listing:

      - Underwriters Laboratories, Inc. (UL)

  - Knockout Configurations:

| Catalog # | Sides | Bottom |
| --- | --- | --- |
| TP5SQ5075 | (12)- 1/2"+3/4" Concentric | (3)- 1/2", (2) 3/4" |
| TP5SQ50100 | (4)-1/2", (8)-1" | (3)- 1/2", (2) 3/4" |
| TP5SQ100125 | (4)-1", (4)1-1/4" | (3)- 1/2", (2) 3/4" |

- Box Support Brackets:

  - Open Box Support- Compatible and suggested for use brackets:

| Manufacturer | Catalog # | Application |
| --- | --- | --- |
| B-Line | BB7-16 | Open box support mounting bracket - 16” stud spacing |
| B-Line | BB7-24 | Open box support mounting bracket - 24” stud spacing |
| B-Line | BB7AP | Alignment plate centers and secures box to the to BB7-16 or BB7-24 brackets |

  - Telescoping Box Support- Compatible and suggested for use brackets:

| Manufacturer | Catalog # | Application |
| --- | --- | --- |
| B-Line | BB2-16 T | Telescoping bracket - 16” stud spacing |
| B-Line | BB2-24 T | Telescoping bracket - 24” stud spacing |
| B-Line | BB2TSC | Box mounting clip used in conjunction with BB2-16T or BB2-24T brackets |
| B-Line | BB2-16 TS | Telescoping bracket - 16” stud spacing with box mounting |
| B-Line | BB2-24TS | Telescoping bracket - 24” stud spacing with box mounting |

- Adapter Plate: Suitable to reduce front opening of box from 5 inch square to allow the use of 4 inch mud rings and plaster rings, Crouse Hinds Catalog # TP5CP

  - Shall have the following characteristics:

    - Materials:

      - Galvanized Steel, 0.0625 in thickness (minimum)

      - Outside Dimensions:

        - 5.06 in (128.5 mm) Width

        - 5.06 in (128.5 mm) Height

        - 0.063 in (1.6 mm) Depth

      - Construction:

        - Stamped/Drawn fabrication

      - Mounting/Attachment Features:

        - For Mounting Plate to Box:  4 screw slots (2 straight and at least 2 angled), suitable to mount on preinstalled box screws with a distance of 2 ¾ in (69.85 mm) between both sets of plate mounting screws.

        - For Mounting Mud Rings or Plaster Rings to Adapter Plate:  4 faceplate tabs with a minimum of 2 #8-32 x ½” preinstalled screws.

      - Testing / Listing:

        - Underwriters Laboratories, Inc. (UL)

- 5 inch Square: Blank Box Covers.

  - 5 inch Square Blank Box Cover, Crouse Hinds Catalog # TP5BC

    - Materials:

      - Galvanized Steel, 0.0625 in thickness (minimum)

      - Outside Dimensions:

        - 5.06 in (128.5 mm) Width

        - 5.06 in (128.5 mm) Height

    - Construction:

      - Stamped fabrication

    - Mounting/Attachment Features:

      - Attachable directly to box

      - 4 screw slots (2 straight and at least 2 angled), suitable to mount on screws that are already in place.

    - Testing / Listing:

      - Underwriters Laboratories, Inc. (UL)

- 4 inch Square Extension Rings: Suitable for use when installed in conjunction with 5 inch square to 4 inch square adapter plate. Also called “mud rings” or “plaster rings”.

  - All extension rings shall have the following characteristics:

    - Materials:

      - Galvanized Steel, 0.0625 in thickness (minimum)

      - Outside Dimensions:

        - 4 in  (minimum) Width

        - 4 in  (minimum) Height

      - Construction:

        - Stamped/Drawn fabrication

    - Mounting/Attachment Features:

      - Attachable directly to Crouse Hinds Adapter Plate (catalog # TP5CP)

      - 4 screw slots, suitable to mount on screws that are already in place.

      - At least 2 faceplate mounting tabs, with tapped holes (6-32) to receive faceplate screws. For 4 Square Extension ring, the tapped holes shall be 8-32.

    - Reversible: Extension Rings shall be capable of being mounted in multiple orientations.

    - Testing / Listing:

      - Underwriters Laboratories, Inc. (UL

PART 3 – EXECUTION

3.01	INSTALLATION

- Installation shall be in accordance with NEC Article 314, CEC and any local codes and manufacturer’s instructions.

END OF SECTION