SECTION 16483c

ADJUSTABLE FREQUENCY DRIVE - CLEAN POWER (CPX) & EGP

- GENERAL

  - SCOPE

    - This specification describes the electrical, mechanical, environmental, agency and reliability requirements for three-phase, Adjustable Frequency Drives (AFD) as specified herein and as shown on the contract drawings.

  - RELATED SECTIONS

  - REFERENCES

    - The adjustable frequency drives and all components shall be designed, manufactured and tested in accordance with the latest applicable standards of UL, CUL, and NEMA.

  - SUBMITTALS - FOR REVIEW/APPROVAL

    - The following information shall be submitted to the Engineer.

      - Dimensioned outline drawing.

      - Schematic diagram.

      - Power and control connection diagram(s)

    - Submit four (4) copies of the above information.

  - SUBMITTALS-FOR INFORMATION

    - When requested by the Engineer the following product information shall be submitted:

      - Descriptive bulletins

      - Product sheets

      - Harmonic Analysis

  - SUBMITTALS-FOR CLOSE-OUT

    - The following information shall be submitted for record purposes prior to final payment.

      - Final as-built drawings and information for items listed in Section 1.04.

      - Installation information.

  - QUALIFICATIONS

    - The supplier of the assembly shall be the manufacturer of the electromechanical power components used within the assembly, such as bypass contactors when specified.

    - For the equipment specified herein, the manufacturer shall be ISO 9001:2015 certified.

    - The supplier of this equipment shall have produced similar electrical equipment for a minimum period of ten (10) years. When requested by the Engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

    - Adjustable Frequency Drives shall be based on EATON EGP & CPX Series for function and quality. Products that are in compliance with the specification and manufactured by others will be considered as “Approved Equal” only if pre-approved by the Engineer fourteen (14) days prior to bid date. Alternate suppliers shall submit documentation showing itemized compliance to the specifications and experience specific to the proposed AFD including a list showing details of the installation, application, location, contact name and telephone number of at least 10 users.

  - REGULATORY REQUIREMENTS

  - DELIVERY, STORAGE, AND HANDLING

    - Equipment shall be handled and stored in accordance with manufacturer's instructions.  One (1) copy of these instructions shall be included with the equipment at time of shipment.

  - FIELD MEASUREMENTS

  - OPERATION AND MAINTENANCE MANUALS

    - Five (5) copies of the equipment operation and maintenance manuals shall be provided.

    - Operation and maintenance manuals shall include the following information:

      - Instruction books

      - Recommended renewal parts list.

      - Drawings and information required by Section 1.06.

  - EXTRA PRODUCTS

- PRODUCTS

  - MANUFACTURERS

    - Eaton

    - ___________

    -  ___________

Naming specific venders does not imply acceptance of their standard products nor relieve them from meeting these specifications in their entirety.

  - ADJUSTABLE FREQUENCY DRIVES (AFD)

    - Where shown on the drawings, adjustable frequency drives 25 through 800 Horsepower (HP), Variable Torque (VT) [select one] Constant Torque (CT) shall have the following features:

      - The AFD shall be rated for 480 Vac. The AFD shall provide microprocessor-based control for three-phase induction motors. The controller’s full load output current rating shall be based on 50-degree C ambient at 250HP and below and 40-degree ambient above 250HP VT and no less than a 2.0 kHz switching frequency to reduce motor noise and avoid increased motor losses. Drive shall have been tested to and UL listed as conforming to the requirements of UL508C at rated load currents and ambient temperature per this specification. Drive shall have a UL listed interrupting rating of [65kaIC] [100kAIC] (pick one)

      - The AFD shall be of the Pulse Width Modulated (PWM) design converting the utility input voltage and frequency to a variable voltage and frequency output via a two-step operation. Adjustable Current Source AFD are not acceptable. Insulated Gate Bipolar Transistors (IGBT’s) shall be used in the inverter section. Bipolar Junction Transistors, GTO’s or SCR’s are not acceptable. The AFD shall run at the above listed switching frequency.

      - The AFD shall have an efficiency at full load and speed that exceeds 95%. The efficiency shall exceed 90% at 50% speed and load. The AFDs shall maintain the line side displacement power factor at no less than 0.96, regardless of speed and load.

      - 18 pulse drive shall include the following protective features, as a minimum: Input line fuses, Metal Oxide Varistor (MOV), and Lineside choke rated 7.5% of rated line current.

      - The AFDs shall have a one (1) minute overload current rating of 110% for variable torque loads [pick one] 150% for constant torque loads.

      - The AFDs shall be capable of operating of operating any NEMA design B squirrel cage induction motor, regardless of manufacturer, with a horsepower and current rating within the capacity of the AFD.

      - The harmonics introduced by the adjustable frequency drives at the point of common coupling (PCC) shall meet the requirements of IEEE519-2014 for General Systems. For purposes of this specification the PCC shall be the utility feeder to the facility where multiple users are served. Short circuit amperes at this point and total demand load are noted on the system one-line drawing.  18 pulse drives shall have manufacturer documented maximum current distortion of 5% to ensure harmonic compliance.

      - For systems with a standby generator, the harmonic distortion shall meet the distortion levels shown in table 2 of IEEE519-2014 for ISC/IL<20. The contractor shall provide the following data for the standby generator in order to perform the calculations:  Voltage, kW, kVA and Subtransient Reactance (X”d), and total maximum demand ampere load for generator operation.

      - A harmonic analysis of the system shall be made consisting of the current and voltage harmonics expected from the addition of the adjustable frequency drives for all harmonics through the 25th per tables 1 and 2 of IEEE519-2014. This analysis shall be included as part of the bid submittal. An integrally mounted18 pulse rectifier with a pre-wired phase shifting transformer shall be required as part of this specification.

- The transformer shall be a single wound transformer rated 480 Volts with a UL recognized 180 degree C insulation system. Required performance shall be obtained without exceeding the above indicated temperature rise in a 50 degree C ambient below 250HP and for 40º C maximum ambient above 250HP.

      - The use of harmonic filter traps, 12 pulse rectifiers, Active filters or Active converter sections is not an acceptable substitute to the 18 pulse drive.  All system components including the 18 pulse rectifier and phase shifting transformer shall be integral to the drive enclosure and shipped from the factory as an assembly.  Separate components do not meet the intent of this specification and will not be considered as equivalent.

      - The AFD shall be able to start into a spinning motor (flying start). The AFD shall be able to determine the motor speed in any direction and resume operation without tripping. If the motor is spinning in the reverse direction, the AFD shall start into the motor in the reverse direction, bring the motor to a controlled stop, and then accelerate the motor to the preset speed.

      - Standard operating conditions shall be:

        - Incoming Power: Three phase, 480 Vac (+10% to -10%) and 60 Hz (+/-5 Hz) power is converted to a fixed potential DC bus level. Maximum input voltage unbalance shall be 0.5% as defined in NEMA MG 1 section 14.35.2

        - Frequency stability of +/-0.05% for 24 hours with voltage regulation of +/-1% of maximum rated output voltage.

        - Speed regulation of +/- 0.5% of base speed.

        - Load inertia dependent carry over (ride through) during utility loss.

        - Insensitive to input line rotation.

        - Humidity: 0 to 95% (non-condensing and non-corrosive).

        - Altitude: 0 to 3,300 feet (1000 meters) above sea level.

        - Ambient Temperature: 0 to 50 C (CT) & 0 to 40 C (VT)

        - Storage Temperature: -40 to 60 C.

      - Control Functions

        - Frequently accessed AFD programmable parameters shall be adjustable from a digital operator keypad located on the front of the AFD. The AFD shall have a 3 line alphanumeric programmable display with status indicators. Keypads must use plain English words for parameters, status, and diagnostic messages. Keypads that are difficult to read or understand are not acceptable, and particularly those that use alphanumeric code and tables. Keypads shall be adjustable for contrast with large characters easily visible in normal ambient light.

        - Standard advanced programming and trouble-shooting functions shall be available by using a personal computer’s RS-232 port and Windows™ based software. In addition the software shall permit control and monitoring via the AFD RS-232 port. The computer software shall be used for modifying the drive setup and reviewing diagnostic and trend information as outlined in this section through section 18. Provide one copy of the advanced programming software.

        - The operator shall be able to scroll through the keypad menu to choose between the following:

          - Monitor

          - Operate

          - Parameter setup

          - Actual parameter values

          - Active faults

          - Fault history

          - LCD contrast adjustment

          - Information to indicate the standard software and optional features software loaded.

        - The following setups and adjustments, at a minimum, are to be available:

          - Start command from keypad, remote or communications port

          - Speed command from keypad, remote or communications port

          - Motor direction selection

          - Maximum and minimum speed limits

          - Acceleration and deceleration times, two settable ranges

          - Critical (skip) frequency avoidance

          - Torque limit

          - Multiple attempt restart function

          - Multiple preset speeds adjustment

          - Catch a spinning motor start or normal start selection

          - Programmable analog output

          - DC brake current magnitude and time

          - Proportional/Integral/Differential (PID) process controller

      - The AFDs shall have the following common system interface input requirements:

        - Inputs - A minimum of six (6) programmable digital inputs, two (2) analog inputs and serial communications interface shall be provided with the following available as a minimum:

          - Remote manual/auto

          - Remote start/stop

          - Remote forward/reverse

          - Remote preset speeds

          - Remote external trip

          - Remote fault reset

          - Process control speed reference interface, 4-20m Adc

          - Potentiometer and 0-10 Vdc speed reference interface

          - RS-232 programming and operation interface port

          - Serial communications capability

        - Outputs – A minimum of two (2) discrete programmable digital outputs, one (1) programmable open collector output, and one (1) programmable analog output shall be provided, with the following available at minimum.

          - Programmable relay outputs with one (1) set of form C contacts for each, selectable with the following available at minimum:

              - Fault

              - Run

              - Ready

              - Reversing

              - Jogging

              - At speed

              - In torque limit

              - Motor rotation direction opposite of commanded

              - Over-temperature

        - Programmable open collector output with available 24VDC power supply and selectable with the following available at minimum:

          - Fault

          - Run

          - Ready

          - Reversing

          - Jogging

          - At speed

          - In torque limit

          - Motor rotation direction opposite of commanded

          - Over-temperature

        - Programmable analog output signal, selectable with the following available at minimum:

          - Output current

          - Output frequency

          - Motor speed

          - Motor torque

          - Motor power

          - Motor voltage

          - DC link voltage

      - Monitoring and Displays

        - The AFD display shall be a LCD type capable of displaying three (3) lines of text and the following thirteen (13) status indicators:

          - Run

          - Forward

          - Reverse

          - Stop

          - Ready

          - Alarm

          - Fault

          - Local

          - Panel

          - Remote

          - Hand

          - Auto

          - Off

        - The AFD keypad shall be capable of displaying the following monitoring functions at a minimum:

          - Output frequency

          - Output speed

          - Motor current

          - Motor torque

          - Motor power

          - Motor voltage

          - DC-link voltage

          - Heatsink temperature

          - Total operating days counter

          - Operating hours (with reset function)

          - Total megawatt hours

          - Megawatt hours (with reset function)

          - Voltage level of analog input

          - Current level of analog input

          - Digital inputs status

          - Digital and relay outputs status

          - Motor temperature rise, percentage of allowable.

      - Protective Functions

        - The AFD shall include the following protective features at minimum:

          - Over-current

          - Over-voltage

          - Inverter fault

          - Under-voltage

          - Phase loss

          - Output phase loss

          - Under-temperature

          - Over-temperature

          - Motor stalled

          - Motor over-temperature

          - Motor under-load

          - Logic voltage failure

          - Microprocessor failure

          - DC injection braking

        - The AFD shall provide ground fault protection during power-up, starting, and running. AFD with no ground fault protection during running are not acceptable.

      - Diagnostic Features

        - Fault History

          - Record and log faults

          - Indicate the most recent first and store up to 9 faults.

      - Optional features to be included in the AFD:

Note to Spec. Writer: Consultant to choose options required from list below

        - HMCP or thermal magnetic breaker to provide a disconnect means. Operating handle shall be flange mounted. The disconnect shall not be mounted on the door. The handle position shall indicate ON, OFF, and TRIPPED condition. The handle shall have provisions for padlocking in the OFF position with at least three (3) padlocks.  Interlocks shall prevent unauthorized opening or closing of the AFD door with the disconnect handle in the ON position. Door handle interlock can be defeated by qualified maintenance personnel. ]

        - Three contactor bypass shall include a drive input disconnect, an AFD input isolation contactor, bypass contactor and an AFD output contactor that is electrically and mechanically interlocked with the bypass contactor. This circuit shall include control logic, status lights and motor over-current relays. The complete bypass system  [Inverter-Off-Bypass] [Hand-Off-Auto with Inverter-Bypass] selector switch(s), and Inverter/Bypass pilot lights shall be packaged with the AFD. The unit may be set up for [Manual] [Automatic] bypass operation upon an AFD trip].

        - AC output contactor to provide a means for positive disconnection of the drive output from the motor terminals.

        - Fused space heaters with thermostat for oversize enclosures to minimize condensation potential upon drive shutdown.

        - [Laminated plastic] [steel] nameplate engraved with user’s identifying name or number for oversize enclosures.

        - Pneumatic process follower allowing motor speed control proportional to a 3-15PSIG pneumatic signal.

        - 120 VAC control to allow AFD to interface with remote dry contacts.

        - Motor dv/dt filter for use on motor cable runs exceeding 100 feet for motors with a peak voltage insulation rating less than 1600 Vac.

              - The dv/dt filter shall be located at the AFD and shall reduce the dv/dt clamp any voltage overshoots of the AFD output. It will return the energy in the voltage overshoots to the AFD Dc bus. A power dissipating resistance device is not acceptable. Filter shall be a EATON

-- OR --

          - A properly sized line reactor shall be installed at the AFD output to reduce dv/dt levels and the resultant peak voltage overshoots at the motor terminals.

        - Dynamic braking control circuitry shall be provided to decelerate the motor faster than the internal losses can absorb. Dynamic braking shall cause an optional resistor bank, when specified; to be switched onto the DC link as required to absorb the regenerative energy. This shall allow the fastest controlled deceleration and/or stop without an over-voltage condition. The resistor bank, when specified, shall be located external to the drive enclosure to prevent overheating of the drive.

        - Resistor bank for dynamic braking load rated for 100 percent braking torque for a 20 percent duty cycle based on a sixty second cycle time.

        - Communication card for interface with [Modbus RTU] [DeviceNet] [CanOpen] [Profibus-DP] [Lonworks] [Modbus TCP ] [Johnson Controls N2 Metasys] [Ethernet/IP] control system.

        - Provide an input EMI filter to minimize conducted electrical noise to meet the requirements of IEC 61800-3.

      - Enclosure

        - The AFD enclosure shall be UL listed type enclosure [NEMA 1] [NEMA 1 filtered and gasketed]. The AFD shall have complete front accessibility with easily removable assemblies.

      - Spare Parts

        - The main logic board, keypad and power supply board shall be supplied as spares, one for each different part number supplied.

      - The AFD manufacturer shall maintain, as part of a national network, engineering service facilities within 100 miles of project to provide start-up service, emergency service calls, repair work, service contracts, maintenance and training of customer personnel.

- EXECUTION

  - EXAMINATION

  - FACTORY TESTING

    - The following standard factory tests shall be performed on the equipment provided under this section. All tests shall be in accordance with the latest version of UL and NEMA standards.

      - All printed circuit boards shall be functionally tested via automatic test equipment prior to unit installation.

      - All inverter power sub-assemblies shall undergo a burn-in test.

      - After all pre-tests have been performed, each complete AFD shall undergo a burn-in test. The drive shall be burned in with a motor load without an unscheduled shutdown.

    - The manufacturer shall provide three (3) certified copies of complete AFD final test reports.

  - INSTALLATION

  - FIELD QUALITY CONTROL

    - Provide the services of a qualified manufacturer's employed Field Service Engineer to assist the Contractor in installation and start-up of the equipment specified under this section.  Field Service personnel shall be factory trained with periodic updates and have experience with the same model of AFD on the job site. Sales representatives will not be acceptable to perform this work. The manufacturer's service representative shall provide technical direction and assistance to the Contractor in general assembly of the equipment, installation as specified in manufacturer’s installation instructions, wiring, application dependant adjustments, and verification of proper AFD operation.

    - The Contractor under the technical direction of the manufacturer’s service representative shall perform the following minimum work.

      - Inspection and final adjustments.

      - Operational and functional checks of AFD and spare parts.

      - The contractor shall certify that he has read the drive manufacturer’s installation instructions and has installed the AFD in accordance with those instructions.

    - The Contractor shall provide three (3) copies of the manufacturer's field start-up report before final payment is made.

  - MAINTENANCE / WARRANTY SERVICE

    - Warranty to commence 24 months from the date of shipment. An additional year to be provided with certified startup.

  - FIELD TESTING

    - Optional field testing

      - The AFD manufacturer shall perform harmonic measurements at the point where the utility feeds multiple customers (PCC) to verify compliance with IEEE519-2014. A report of the voltage THD and current TDD shall be sent to the engineer. The contractor shall provide labor, material, and protection as needed to access the test points. The readings shall be taken with all drives and all other loads at full load, or as close as field conditions allow.

  - TRAINING

    - The Contractor shall provide a training session for up to ____ owner's representatives for ____ normal workdays with a maximum of ____ trips at a job site location determined by the owner. Training and instruction time shall be in addition to that required for start-up service.

    - The manufacturer’s qualified representative shall conduct the training.

    - The training program shall consist of the following:

      - Instructions on the proper operation of the equipment.

      - Instructions on the proper maintenance of the equipment.

 Note to Spec. Writer – Insert data in blanks

 Note to Spec. Writer - Optional

 Note to Spec. Writer – Optional

 Note to Spec. Writer – Select one

 Note to Spec. Writer – Select one

 Note to Spec. Writer – Insert data in blanks