## Controls Input Sheet
Enter the input data for your project into the yellow cells below. When finished, click on the "Input Sheet" tab to proceed
Connected Lighting Design Parameters | Input Data
Are lights going to be Indoor or Outdoor? | Indoor
How many hours is area scheduled to be non operational (Scheduling)? | 8 | Scheduled ON/OFF: management of time scheduling to optimize energy usage
How many hours is area going to have irregular/ low frequency traffic during operational hours (Occupancy)? | 4 | Occupancy sensing: motion sensing to monitor occupancy of a site or for control of infrequently used areas
% of time lights will be ON in irregular/ low frequency traffic areas during operational hours (Occupancy) | 70% | Daylight harvesting: photo sensing measures ambient light levels and adjusts light output accordingly, saving energy and extending fixture life
How many hours Day Light is present in operational areas (Day Light Harvesting) | 8
For operational areas where daylight is present, what is the assumed average "dimmed %" level throughout the day? (70% dimmed = 70% light savings | 50%
Total Savings(Over assumed 24 hours of operation) | 55%
|  |  | Scheduling | Dimming | Occupancy | Day Light Harvesting | Dimming Level | Daylight Harvesting Option
Notes for inputting data aove |  |  | 0 | 0 | 0 | 0 | 0% | Indoor
1. Sum of Control inputs to be <=24 hours |  |  | 4 | 4 | 4 | 4 | 10% | Outdoor
2. Use of control input to be based upon realiastic business scenario, Each control input for calculation purposes is a stand alone input (except for % inputs). |  |  | 8 | 8 | 8 | 8 | 20%
3. Scheduling - enables site to schedule time when lights will be On or Off. Fill in this field with Time-Hours/day lights will be OFF |  |  | 12 | 12 | 12 | 12 | 30%
4. Occupancy - Number of hours in a day area is expected to be vacant (during operational hours). |  |  | 16 | 16 | 16 | 16 | 40%
5. Daylight harvesting - Daylight harvesting senses natural light in the area to adjust light output of fixtures |  |  | 20 | 20 | 20 | 20 | 50%
6. Dimming- Hours of day dimming is used to reduce light output levels - Can be set to % light output needed in facility |  |  | 24 | 24 | 24 | 24 | 60%
70%
80%
90%
100%

## Input Sheet
Enter the input data for your project into the yellow cells below. When finished, click on the "Savings and TCO Summary" tab to view your realized cost savings and ROI
Design Parameters |  |  |  | Input Data |  | Input Watts | Ave Lamp Life
1 | Customer or Project Name |  |  | Customer Name
2 | Traditional Lamp Source (Click Cell to Select Lamp Source) |  |  | 175W MH | 175W MH | 208 | 15000 |  | 175W MH
3 | Input quantity of LED fixtures used for the project ? |  |  | 1000
4 | Input quantity of HID/HPS fixtures being replaced or retrofitted ? |  |  | 1000
5 | Enter a cost of the existing luminaire ($ each) |  |  | 300
6 | Cost of replacement lamps in ($) |  |  | 25
7 | Cost of disposal per lamp ($) |  |  | 2
8 | Time per fixture for lamp maintenance (Hours) |  |  | 1
9 | How many people are required for lamp maintenance ? |  |  | 2
10 | Enter the labor rate ($ per Hour) |  |  | 80
11 | What is the energy cost on site ? ( $ / kWhr ) |  |  | 0.09
12 | Enter lighting hours of operation per day (12, 24 etc) |  |  | 24 |  | 8736 | Operating Hours Per Year
13 | Is LED lighting being used in an air conditioned area requiring cooling (If Y, then input ROWS 13-17) |  |  | NO | YES
14 | Fraction of year of the cooling season (in weeks) |  |  | 30 | NO
15 | Lighting load met by mechanical cooling (How much of lighting system's heat must be removed by cooling) |  |  | 90%
16 | Temperature to be maintained within the air conditioned building (deg F) |  |  | 50 | 10
17 | Ambient Temperature (deg F) |  |  | 80 | 26.6667
18 | Coefficient of Performance of cooling system (COP) |  |  | 1.6989 | 1.6989
19 | Maximum average temperature to which LED fixture will be exposed throughout the year (deg F) |  |  | 104 |  |  | LED Indoor | LED outdoor
20 | LED Light Source (Click Cell to Select LED Source) |  |  | VMV 7L - 58W | VMV 7L - 58W | 58.4 | 172700 | 131000 | VMV 7L - 58W
21 | LED Luminaire Cost |  |  | 704.4
22 | LED Installation Cost (Total Labor for installing all LED Fixtures) |  |  | 200000
23 | Other Fixed Cost Assosciated with Lamp Maintenance (Lift Rental, Scaffolding etc) |  |  | 0
24 | Manufacturing or process downtime opportunity cost due to loss of lighting ($) |  |  | 0
25 | Estimated Utility rebate for the project ($) |  |  | 7500
26 | Estimated EPACT (Section 179D) tax savings for the project ($) |  |  | 7500 |  |  | Connected Indoor | Connected Outdoor
27 | Connected LED Light Source (Click Cell to Select LED Source) |  |  | VMV 7L - 58W | VMV 7L - 58W | 58.4 | 259050 | 262000
28 | Input Quantity of Sensor Units |  |  | 200
29 | Sensor Unit Cost |  |  | 1130.2
30 | Input Quantity of Control only Units |  |  | 800
31 | Control Unit Cost |  |  | 1028.22
32 | Other Fixed Cost Assosciated with Lamp Maintenance (Lift Rental, Scaffolding etc) |  |  | 0
33 | Other Fixed Cost Associated with Solution Hardware installation (Gateway, Server, Software-Windows) |  |  | 20000
34 | Cost Associated with Drawing/ Engineering Services (Preinstallation) |  |  | 3000
35 | Commissioning Cost |  |  | 2500
36 | Scheduling (Saving Hours/ Day) |  |  | 8 |  | 2912 |  | 55%
37 | Occupancy (Saving Hours/ Day) |  |  | 1.2 |  | 436.8
38 | Day Light harvesting (Saving Hours/ Day) |  |  | 4 |  | 1456
39 | Overall Energy Savings |  |  | 55%
CHART A
| Lamp Source | Input Watts | Ave Lamp Life | [16 empty] | Connected Outdoor
A | 100W HPS | 130 | 24000 |  |  | LED INDOOR |  |  |  |  | LED OUTDOOR |  |  |  | Connected Indoor | [5 empty] | Lamp Source | Input Watts | Ave Lamp Life
B | 150W HPS | 188 | 24000 |  |  |  | Lamp Source | Input Watts | Ave Lamp Life |  |  | Lamp Source | Input Watts | Ave Lamp Life |  | Lamp Source | Input Watts | Ave Lamp Life |  | A | VMV 3L - 26W | 26.4 | 262000
C | 200W HPS | 240 | 24000 |  |  | A | VMV 3L - 26W | 26.4 | 172700 |  | A | VMV 3L - 26W | 26.4 | 131000 | A | VMV 3L - 26W | 26.4 | 259050 |  | B | VMV 5L - 42W | 42.4 | 262000
D | 250W HPS | 295 | 24000 |  |  | B | VMV 5L - 42W | 42.4 | 172700 |  | B | VMV 5L - 42W | 42.4 | 131000 | B | VMV 5L - 42W | 42.4 | 259050 |  | C | VMV 7L - 58W | 58.4 | 262000
E | 100W MV | 125 | 24000 |  |  | C | VMV 7L - 58W | 58.4 | 172700 |  | C | VMV 7L - 58W | 58.4 | 131000 | C | VMV 7L - 58W | 58.4 | 259050 |  | D | VMV 9L - 74W | 74.4 | 235200
F | 175WMV | 205 | 24000 |  |  | D | VMV 9L - 74W | 74.4 | 119000 |  | D | VMV 9L - 74W | 74.4 | 117600 | D | VMV 9L - 74W | 74.4 | 178500 |  | E | VMV 11L-90W | 90.4 | 174600
G | 250W MV | 285 | 24000 |  |  | E | VMV 11L-90W | 90.4 | 86400 |  | E | VMV 11L-90W | 90.4 | 87300 | E | VMV 11L-90W | 90.4 | 129600
H | 6 Lamp 54W T5 | 372 | 30000
I | 70W MH | 90 | 15000 |  |  |  | Champ VMV LED Fixture Lifetime Analysis - INDOOR (90% Reliability) |  |  |  |  | Champ VMV LED Fixture Lifetime Analysis - OUTDOOR (90% Reliability) |  |  |  | Connected Lighting Champ VMV LED Fixture Lifetime Analysis (INDOOR)/(90% Reliability) |  |  |  |  | Connected Lighting Champ VMV LED Fixture Lifetime Analysis (OUTDOOR)/(90% Reliability) |  |  | Column1 | Column2
J | 100W MH | 125 | 15000 |  |  |  | Model | Ambient Temp C | Ambient Temp F | Fixture Life (Hrs) |  | Model | Fixture Life (Hrs) |  |  | Model | Ambient Temp C | Ambient Temp F | Fixture Life (Hrs) |  | Model | Fixture Life (Hrs) |  | C | F
K | 150W MH | 185 | 15000 |  |  |  | VMV 3L - 26W | 25C | 77 | 362400 |  | VMV 3L - 26W | 131000 |  |  | VMV 3L - 26W | 25C | 77 | 543600 |  | VMV 3L - 26W | 262000 |  | 25C | 77
L | 175W MH | 208 | 15000 |  |  |  | VMV 3L - 26W | 40C | 104 | 172700 |  | VMV 5L - 42W | 131000 |  |  | VMV 3L - 26W | 40C | 104 | 259050 |  | VMV 5L - 42W | 262000 |  | 40C | 104
M | 250W MH | 288 | 20000 |  |  |  | VMV 3L - 26W | 55C | 131 | 81300 |  | VMV 7L - 58W | 131000 |  |  | VMV 3L - 26W | 55C | 131 | 121950 |  | VMV 7L - 58W | 262000 |  | 55C | 131
N | 320W MH | 368 | 20000 |  |  |  | VMV 3L - 26W | 65C | 149 | 47800 |  | VMV 9L - 74W | 117600 |  |  | VMV 3L - 26W | 65C | 149 | 71700 |  | VMV 9L - 74W | 235200 |  | 65C | 149
O | 400W MH | 452 | 20000 | [8 empty] | VMV 11L-90W | 87300 | [7 empty] | VMV 11L-90W | 174600
Q | 55W Induction | 59.8 | 100000 |  |  |  | Model | Ambient Temp | Ambient Temp F | Fixture Life (Hrs) | [5 empty] | Model | Ambient Temp | Ambient Temp F | LED Case Temp
R | 85W Induction | 92 | 100000 |  |  |  | VMV 5L - 42W | 25C | 77 | 362400 | [5 empty] | VMV 5L - 42W | 25C | 77 | 543600
S | 165W Induction | 162 | 100000 |  |  |  | VMV 5L - 42W | 40C | 104 | 172700 | [5 empty] | VMV 5L - 42W | 40C | 104 | 259050
T | 70W PSMH | 90 | 15000 |  |  |  | VMV 5L - 42W | 55C | 131 | 81300 | [5 empty] | VMV 5L - 42W | 55C | 131 | 121950
U | 100W PSMH | 125 | 15000 |  |  |  | VMV 5L - 42W | 65C | 149 | 47800 | [5 empty] | VMV 5L - 42W | 65C | 149 | 71700
V | 150W PSMH | 185 | 15000
W | 175W PSMH | 208 | 15000 |  |  |  | Model | Ambient Temp | Ambient Temp F | Fixture Life (Hrs) | [5 empty] | Model | Ambient Temp | Ambient Temp F | LED Case Temp
X | 250W PSMH | 288 | 15000 |  |  |  | VMV 7L - 58W | 25C | 77 | 362400 | [5 empty] | VMV 7L - 58W | 25C | 77 | 543600
Y | 320W PSMH | 368 | 20000 |  |  |  | VMV 7L - 58W | 40C | 104 | 172700 | [5 empty] | VMV 7L - 58W | 40C | 104 | 259050
Z | 400W PSMH | 452 | 20000 |  |  |  | VMV 7L - 58W | 55C | 131 | 81300 | [5 empty] | VMV 7L - 58W | 55C | 131 | 121950
[7 empty] | VMV 7L - 58W | 65C | 149 | 47800 | [5 empty] | VMV 7L - 58W | 65C | 149 | 71700
Notes: | [6 empty] | Model | Ambient Temp | Ambient Temp F | Fixture Life (Hrs) | [5 empty] | Model | Ambient Temp | Ambient Temp F | LED Case Temp
Be sure replacement time includes time for approvals, down time, paperwork, lock out tag out, man lift, etc. | [6 empty] | VMV 9L - 74W | 25C | 77 | 315500 | [5 empty] | VMV 9L - 74W | 25C | 77 | 473250
Use the fully loaded labor rate | [6 empty] | VMV 9L - 74W | 40C | 104 | 119000 | [5 empty] | VMV 9L - 74W | 40C | 104 | 178500
Many Harsh and Hazardous locations require 2 person teams | [6 empty] | VMV 9L - 74W | 55C | 131 | 52000 | [5 empty] | VMV 9L - 74W | 55C | 131 | 78000
[7 empty] | VMV 9L - 74W | 65C | 149 | 30500 | [5 empty] | VMV 9L - 74W | 65C | 149 | 45750
[7 empty] | Model | Ambient Temp | Ambient Temp F | Fixture Life (Hrs) | [5 empty] | Model | Ambient Temp | Ambient Temp F | LED Case Temp
[7 empty] | VMV 11L-90W | 25C | 77 | 315500 | [5 empty] | VMV 11L-90W | 25C | 77 | 473250
[7 empty] | VMV 11L-90W | 40C | 104 | 86400 | [5 empty] | VMV 11L-90W | 40C | 104 | 129600
[7 empty] | VMV 11L-90W | 55C | 131 | 40300 | [5 empty] | VMV 11L-90W | 55C | 131 | 60450
[7 empty] | VMV 11L-90W | 65C | 149 | 25300 | [5 empty] | VMV 11L-90W | 65C | 149 | 37950
Note on I20: Typical Value for most lighting systems
Note on I23: This is based off Theoretical max efficiency * 10%. Typical COP values range from 2-4 depending upon type of system and heating/cooling load. COP is defined as the cooling or heating load handled by unit for every unit of power consumed (Efficiency of HVAC system)
Note on J23: Anshuman Bhargava: This is based off Theoretical max efficiency * 10%. Typical COP values range from 2-4 depending upon type of system and heating/cooling load. COP is defined as the cooling or heating load handled by unit for every unit of power consumed (Efficiency of HVAC system)
Note on I24: Cannot exceed 149F or 65C operating ambient temperature
Note on I27: Bhal, Hemendra: Using $200/ LED change. ~1-2 Hours (Employee)*$80/hour

## Savings and TCO Summary
Customer Name
Champ® VMV LED Connected Lighting - ROI Calculator
Energy & Maintenance Savings ( For the life of Connected Lighting System)
Energy Savings | [5 empty] | 175W MH |  | LED Over HID |  | Connected LED Over HID |  | Connected LED Over LED
Annual energy consumption (kWhr) | [5 empty] | 1817088 |  | 510182.4 |  | 229582.08 |  | 229582.08
Annual energy cost ($) | [5 empty] | 163537.92 |  | 45916.416 |  | 20662.3872 |  | 20662.3872
Energy Cost over life of lighting System | [5 empty] | 4849416 |  | 1361566.8 |  | 612705.06 |  | 612705.06
Air Cooling energy savings due to switching over to LED lighting (Kwhr/yr) | [7 empty] | 0 |  | 0 |  | 0
Air Cooling energy savings due to switching over to LED lighting ($/yr) | [7 empty] | 0 |  | 0 |  | 0
Annual Energy Savings ($) | [7 empty] | 117621.504 |  | 142875.5328 |  | 25254.0288
Energy Savings over Life of the LED System ($) | [7 empty] | 3487849.2 |  | 4236710.94 |  | 748861.74
Reinvestment & Maintenance Savings | [5 empty] | 175W MH |  | LED Over HID |  | Connected LED Over HID |  | Connected LED Over LED
Years of Maintenance Free Operation | [5 empty] | 0.94437 |  | 19.7688 |  | 29.6532 |  | 29.6532 |  | 1.5
Annual Cost of Replacement Lamps ($) | [5 empty] | 28590.5455 |  | 0 |  | 0 |  | 0
Annual Fixed Maintenance Costs | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | fixture | 100 | 100
Annual Labor Costs ($) | [5 empty] | 169425.4545 |  | 0 |  | 0 |  | 0 |  | hours per year | 8736 | 8736
Reinvestment Savings | [7 empty] | -889400 |  | 0 |  | 889400
Annual Maintenance Savings ($) | [7 empty] | 198016 |  | 198016 |  | 0 |  | wattage | 29 | 26.4 | savings hours
Maintenance & Reinvestment Savings over Life of Product/ System | [7 empty] | 4982400 |  | 5871800 |  | 889400 |  | kwh | 25334.4 | 10956 | 4586
Total Cost of Ownership Comparison
|  | 175W MH | LED | CONNECTED LED |  |  |  | Total $ Savings LED Over HID |  | Total $ Savings Connected over HID |  | Total $ Savings Connected over LED
| Initial Investment | 300000 | 704400 | 1074116 |  |  | Energy Savings: | 3487849.2 |  | 4236710.94 |  | 748861.74
| Utility Rebate | 0 | -7500 | -7500 |  |  | Investment, Labor & Material Savings: | 4982400 |  | 5871800 |  | 889400
| Tax Rebate | 0 | -7500 | -7500 |  |  | Total Savings: | 8470249.2 |  | 10108510.94 |  | 1638261.74
| Net Investment | 300000 | 689400 | 1059116 |  |  | Initial Investment: | -404400 |  | -774116 |  | -369716
| Total Lighting Energy Costs | 4849416 | 1361566.8 | 612705.06 |  |  | Estimated Utility Rebate: | 7500 |  | 7500 |  | 0
| Incremental Air Cooling Energy Costs | 0 | 0 | 0 |  |  | Estimated Tax Rebate: | 7500 |  | 7500 |  | 0
| Total Maintenance Costs | 4982400 | 0 | 0 |  |  | Total $ Return: | 8080849.2 |  | 9349394.94 |  | 1268545.74
| Total Cost of Ownership | 10131816 | 2050966.8 | 1671821.06
| Payback Period on the Incremental LED Cost (Years) |  |  |  | 1.3632
| Payback Period on the Entire LED Installation (Years) |  |  |  | 2.4135
| Payback Period on the Incremental Connected LED Cost over HID (Years) |  |  |  | 2.2269
| Payback Period on the Incremental Connected LED Cost over LED(Years) |  |  |  | 6.692
Equivilant Environmental Impact (LED)*
CO2 Emissions (lbs): |  | 5371287.768 | [6 empty] | Fewer Cars on the Road: |  |  |  | 468.2901
(tons): |  | 2685.6439
[9 empty] | Acres of Trees Planted: |  |  |  | 665.9172
Coal Emissions (lbs): |  | 2607421.2466
(tons): |  | 1303.7106 | [8 empty] | # Housholds Annual Electricity Usage: |  | 503.8731
*Based on Environmental Protection Agency (EPA) emissions factor assumptions.
Equivilant Environmental Impact (Connected Lighting)*
CO2 Emissions (lbs): |  | 6524534.8476 | [6 empty] | Fewer Cars on the Road: |  |  |  | 568.8348
(tons): |  | 3262.2674
[9 empty] | Acres of Trees Planted: |  |  |  | 808.8935
Coal Emissions (lbs): |  | 3167249.926
(tons): |  | 1583.625 | [8 empty] | # Housholds Annual Electricity Usage: |  | 612.0577
*Based on Environmental Protection Agency (EPA) emissions factor assumptions.
Note on H15: 50% of HID fixtures fail after reaching its economic rated life

## Scenarios
Champ® VMV LED Connected Lighting - Application scenarios
EXAMPLE 1 |  | EXAMPLE 2 |  | EXAMPLE 3
Factory indoor location with two shift operation • 8 hours operational with 100% of lights ON • 8 hours utilizing Daylight harvesting at 70% dimming • 8 hours lights OFF with scheduling |  | Factory outdoor location with 16 hours continuous operation • 16 hours operational with 100% of lights ON • 8 hours utilizing Daylight harvesting at 80% dimming |  | Warehouse indoor location with two shift operation • 16 hours operational with 25% of lights ON • 8 hours lights OFF with scheduling
VMV7L Connected Lighting |  | VMV7L Connected Lighting |  | VMV7L Connected Lighting
Area Location | Indoor Factory | Area Location | Outdoor | Area Location | Indoor Warehouse
Scheduling (nonoperational hours) | 8 | Scheduling (nonoperational hours) | 0 | Scheduling (nonoperational hours) | 8
Occupancy (operational hours) | 8 | Occupancy (operational hours) | 16 | Occupancy (operational hours) | 16
Occupancy - % Time Lights ON | 100% | Occupancy - % Time Lights ON | 100% | Occupancy - % Time Lights ON | 25%
Day Light Harvesting hours | 8 | Day Light Harvesting hours | 8 | Day Light Harvesting hours | 0
Day Light Harvesting %Dimmed Level | 70% | Day Light Harvesting %Dimmed Level | 80% | Day Light Harvesting %Dimmed Level | 70%
Total Operating Hours | 8736 | Total Operating Hours | 8736 | Total Operating Hours | 8736
Annual Energy Savings from Controls Solution | 4950.4 | Annual Energy Savings from Controls Solution | 2329.6 | Annual Energy Savings from Controls Solution | 7280
Total Annual Consumption (Hours) | 3785.6 | Total Annual Consumption (Hours) | 6406.4 | Total Annual Consumption (Hours) | 1456
# LEDs | 1000 | # LEDs | 1000 | # LEDs | 1000
Annual Kwh consumption | 221079.04 | Annual Kwh consumption | 374133.76 | Annual Kwh consumption | 85030.4
Per Kwh cost of energy | 0.09 | Per Kwh cost of energy | 0.09 | Per Kwh cost of energy | 0.09
Total Cost of Energy with Connected lighting/ Year | 19897.1136 | Total Cost of Energy with Connected lighting/ Year | 33672.0384 | Total Cost of Energy with Connected lighting/ Year | 7652.736
Total LED Cost with 24 hour operation/ Year | 45916.416 | Total LED Cost with 24 hour operation/ Year | 45916.416 | Total LED Cost with 24 hour operation/ Year | 45916.416
Energy savings with Connected Solution/ Year | 26019.3024 | Energy savings with Connected Solution/ Year | 12244.3776 | Energy savings with Connected Solution/ Year | 38263.68