# Product Specification Guide – Champ® LED VMV Luminaires Hi-Lumen

# SECTION 26 54 00 – Classified Location Lighting

GENERAL

SCOPE

Furnishing, installation, and assembly of lighting fixtures for areas classified as hazardous.

REFERENCES

National Fire Protection Association (NFPA):

NFPA 70	National Electrical Code (NEC)

CSA Group

Canadian Electrical Code (CEC)

CSA C22.2 No. 137  Luminaires for use in Hazardous (Classified) Locations

Underwriters Laboratories, Inc. (UL):

UL844		Luminaires for use in Hazardous (Classified) Locations

UL1598	Luminaires

UL1598A	Supplemental Requirements for Luminaires for Installation on Marine Vessels

UL8750	Light Emitting Diode (LED) Equipment for Use in Lighting Products

UL50		Enclosures for Electrical Equipment, Non-Environmental Considerations

UL50E		Enclosures for Electrical Equipment, Environmental Considerations

National Electrical Manufacturers Association (NEMA):

International Electrotechnical Commission (IEC):

60079		Explosive Atmospheres

60529		IP Degree of Protection

60598		Luminaires - General requirements and tests

European Commission (EU):

Directive 94/9/EC	      Equipment for explosive atmospheres (ATEX)

Directive 2004/108/EC     EMC certification

SUBMITTALS - FOR REVIEW/APPROVAL

The following information shall be submitted to the Engineer.

Manufacturer’s descriptive literature and technical specifications for each product

Manufacturer’s product drawing (2D or 3D), when requested

Manufacturer’s installation and maintenance document

QUALIFICATIONS

The supplier of the assembly must be the manufacturer of the major components within the assembly.

For the equipment specified herein, the manufacturer must be ISO 9001 certified.

The manufacturer of this equipment must have produced similar electrical equipment for a minimum period of five (5) years. When requested by the Engineer, an acceptable list of installations with similar equipment will be provided demonstrating compliance with this requirement.

Products must be free of defects in material and workmanship.

REGULATORY REQUIREMENTS

DELIVERY, STORAGE, AND HANDLING

Store products in manufacturer’s unopened packaging until ready for installation

PRODUCTS

MANUFACTURERS

Acceptable Manufacturers:

Eaton’s Crouse-Hinds Business

1201 Wolf Street

Syracuse, NY 13208

(866) 764-5454

www.crouse-hinds.com

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

ELECTRICAL REQUIREMENTS

Champ® VMV LED Luminaires:

Standard input driver voltage of 100-277 VAC, 50/60 Hz with optional drivers having 347-480 VAC.

Power factor > 0.95 @ 277 VAC & THD < 13% @ 277 VAC.

DC input of 108-250 in addition to above mentioned AC input must be available on a single driver.

System efficiency: minimum of 100 lumens per watt (LPW) for Type V optical configuration fixtures and 95 LPW for Type I and Type III optical configuration fixtures.

LED fixtures will include 3 or 6 pole terminal blocks with clearly marked input/output for line, neutral and ground electrical connections for 100-277 VAC input range options.

Drivers must have an L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range).

Discrete LEDs must be connected in multiple series circuits by multiple drivers or power supplies to increase fixture’s overall system reliability and prevent complete loss of illumination in the event of the failure of a single driver.

The drivers will have inbuilt 0-10 dimming function and capable of being wired to an external occupancy sensing/dimming device.

Maximum desired input power (wattage) and current (amps) by fixture type @ 120VAC & 277VAC:

| Lumen Levels (Average) | Wattage @ 120VAC | Amperes @ 120VAC | Wattage @ 277VAC | Amperes @ 277VAC |
| --- | --- | --- | --- | --- |
| 1300 | 132 | 1.1 | 135 | 0.5 |
| 1700 | 170 | 1.5 | 170 | 0.65 |
| 2100 | 198 | 1.7 | 200 | 0.75 |
| 2500 | 235 | 2.0 | 240 | 0.90 |

material requirements

Champ® VMV LED Luminaires:

LED housing assembly and heat sink must be of die cast aluminum with epoxy powder coat for corrosion protection and heat dissipation.

Fixture shall have external surface of copper-free anodized aluminum and silicon type gaskets between the lens and LED board assembly, driver and LED housing for protection against acids (including acetic acid), sulfur, water (liquid and vapor form), hydrocarbons and chlorine.

LED board assembly lens cover must be made of heat- and impact-resistant glass. Shatterproof Teflon coating or polycarbonate material options will be available for glass prohibited applications.

Fixture must utilize silicon type gaskets between the driver and LED housing as well as the lens cover and LED board for ingress protection against dust and water.

Fixtures must not contain mercury or any other hazardous chemicals.

Diffused lens option must be available for applications requiring low glare.

Optional wire guard accessory must be of stainless steel.

Optional cone top hat must be provided for applications in dusty environments.

design and performance requirements

Champ® VMV LED Luminaires:

The fixture design must have serviceable drivers.

Fixture must be available with cone shaped top hat for dust shedding in food and beverage industrial applications.

Fixture must have vertical fin design at the housing to maximize heat dissipation and facilitate dust shedding.

All wiring must be concealed in the top hat and driver housing.

Fixture must be total cut-off type to reduce light spill and glare.

Lever-lock connectors must be utilized for wiring connection from LEDs to drivers and from drivers to terminal block and mains.

Standard 3 pole or 6 pole terminal block with line, neutral and ground connections must be utilized for 100-277 VAC fixture construction.

Fixture must have a separate driver housing and gasket joint construction for water ingress and thermal protection.

Thermal pad must be utilized instead of thermal grease for heat dissipation from PCB board.

Optics must have ability to be clocked and preset to various positions from factory to accommodate alignment with conduit wiring entries to the fixture top hat.

Fixtures must have multiple discrete LED series circuits connected to two or more drivers for redundancy and to avoid complete loss of illumination in the event of a driver failure.

Fixture must have domed lens construction to increase optical efficiency.

Drivers must have a L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range).

Fixtures must have a start-up and operating ambient temperature range of -40°C to +55ºC.

Water must not enter the compartment that houses wiring, wiring devices or lamps under any condition of exposure other than submersion.

Fixtures must have DesignLights Consortium® approval and listing for cool white 100-277 VAC /UNV1 options for all lumen levels.

Fixture must successfully be tested for 3 axis (5G) vibration testing to withstand extreme vibration-prone environments.

Single fixture construction meeting both NEC and IEC certifications. Fixtures will have the following T codes or higher various voltages and ambient temperatures.

| Lamps/Lumen Output | Ambient | Class I, Division 2 | Class II, Division 1 | Simultaneous Rating | Class I Zone 2 AEx Na nR; | Zone 21 AEx tb IIIC; |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Class I, Division 2 and class II, Division 1 | Ex nA nR | Class III. Div 1; Class II, Div1, Group E,F, and G |
| 13L,17L | 40°C | T4A | T5 | T4A | T6 | T66°C |
| 13L,17L | 55°C | T4 | T4A | T4 | T5 | T81°C |
| 21L, 25L | 40°C | T4A | T5 | T4A | T6 | T71°C |
| 21L, 25L | 55°C | T4 | T4A | T4 | T5 | T86°C |

2.05 led system and optics requirements

Champ® VMV LED Luminaires:

LED fixtures must have correlated color temperature of 5000K or 3000K.

Fixtures must use discrete Luxeon M power emitters with a minimum CRI of 70 @ 5000K and L70 of 400,000 @ 55°C ambient.

LED fixtures must have a rated life of a minimum 60,000 hours @ operating ambient temperature of 55°C.  This must be a complete system life including life of drivers.

External drivers must be utilized with a minimum of 3” separation from LED PCB circuit for effective heat dissipation and increased reliability. The drivers must be field replaceable in hazardous and industrial locations.

Fixtures must have redundant power drivers so that loss of an individual driver does not cause complete loss of illumination.

Custom optics over each discrete LED and domed lens must be provided for maximum optical efficiency.  Refractors and reflectors must not be utilized to achieve specific optical patterns.

The following optional optical patterns must be made available as options to maximize the light distribution and intensity (lux/footcandles) for different high bay/low bay, wall, pole, pendant and ceiling mount applications:

            - Type I - long and rectangular for hallways, walkways, loading docks, conveyors etc.

            - Type III - wall Mount forward throw light distribution minimizing spillover on the wall.

            - Type V - regular circular distribution pattern for high/low bay indoor and outdoor ceiling or pendant mount lighting.

The following lens options must be available with standard LED light fixture:

            - Clear glass for standard offering

            - Polycarbonate to meet food/grain requirements

            - Diffused glass (non-glare)

            - Teflon coated shatterproof glass

The fixture must have following nominal lumen output ratings for cool white color, Type V optics and standard clear glass lens with a +/- tolerance.

| System Configuration | Nominal Lumen Output @ 25C (+/- 10% tolerance) |
| --- | --- |
| 13000 lumens | 13,266 |
| 17000 lumens | 18,793 |
| 21000 lumens | 22,110 |
| 25000 lumens | 26,531 |

The lumen, efficacy, wattage, CRI, CCT, Power factor, THD, amperage, insitu temperature data and L70 lifetime must be validated from third party LM79, LM80 and TM21 calculation reports.

PART 3 EXECUTION

INSTALLATION

The fixture must have retrofit capability with existing Eaton’s Crouse-Hinds HID and LED fixture top hats using stainless steel bolt and threaded housing for positive retention.

The fixture must be provided with a holding clip to support the housing assembly to top hat during field installation process.

The fixture must mount to all existing modules in the field:

Pendant, wall and ceiling mount options with ¾” and 1” conduit hub size

25° and 90° stanchion mount options with 1.5” and 1.5” 25 deg. hub

Trunnion mount with 0°, 22.5° and 45° angles.  The trunnion must not be adjustable to an angle greater than ±90° to meet temperature requirements.