CEAG ExLin Linear LED Fixtures –

Key Specifiable Features

Certification:

Marking accd. to 2014/34/EC: 	Ex II 2 G Ex eb ib q op is IIC T4 Gb

Marking to IECEx: 	Ex eb ib q op is IIC T4 Gb

LED module: 	U certificate available for the LED module

Control gear: 	U certificate available for the control gear

Mechanical:

Permissible ambient temperature: 	From -40 °C up to +55 °C, depending on version

Enclosure material: 	Glass-fibre reinforced polyester (GRP)

Housing color: 	Grey and black

LED cover material: 	Glass, polycarbonate on request

LED cover transparency: 	Clear or frosted

Cable glands: 	Ex-e cable glands M25 for cables from Ø 8 - 17 mm, option: M20 metal thread for metallic cable glands or M25 metallic cable glands

Terminals: 	Up to 6 mm², easy wiring due to spacious terminal compartment

Heatsink: 	The heat sink shall be located directly under the LED PCB, in order to ensure highest led lifetime and efficiency

Design:	The fitting shall be designed as a modular fitting. The driver chamber shall be located separately to the LED module

Degree of protection accd. to EN 60529: 	IP66

Dimensions (L x W x H): 	Max. 901 x 201 x 115 mm

Weight: 	Max. 7 Kg for fitting with lumen output below 7000 lm

Max. 9 kg for fitting with lumen output >7000 lm

Lighting performance:

Rated luminous flux of the luminaire : 	From ca  2700lm up to ca 8100lm

Luminiare efficiency : 	Up to 120 lm/W

LED lifetime@25°C: 	L90: 100 kh

LED lifetime@55°C: 	L85: 75 kh

Color rendering index: 	70, 80 on request

Corelated color temperature: 	5000 K. Others on request.

Optic: 	Standard, narrow and wide beam available

Performance at high temperature: 	No active lumen reduction at high temperature

Ex Protection: 	The LED module shall have a U certification. The LED string shall be protected according to “i” protection

Electrical performance:

Rated voltage: 	110 - 254 V AC 50/60 Hz / 110 - 250 V DC

Driver lifetime@25°C:	C5: 100,000h

Driver lifetime@55°C:	C10: 75,000h

Power factor @ 230V:		≥0.95

THD: 		<8%

Insulation class: 		I

Inrush current: 		6 A for 1ms for lumen output <7000 lm.

10 A for 1ms for lumen output >7000 lm

Surge: 		The fitting shall have a surge protection of 4 kV line-to-line and line-to-ground based on EN61000-4-5

Installation & Maintenance:

Construction: 	Modular design that allows:

- Independent replacement or upgrade of LED module and control gear

- Conversion of different optic

Mounting: 	2 x M8 metal thread at 400 mm distance

Kit for installing at 700 mm distance as option

Locking: 	Screw located on the light emitting side of the fitting, for easy accessability

Terminal: 	Terminal accessibility without opening the driver chamber

Control gear chamber: 	Cover without external hinges

Cover can be fixed and opened on both sides of the fitting

Maintenance: 	LED module and control gear separately and independently accessable