# Product Specification Guide – Hazard•Gard® XPL Linear LED Lighting

# SECTION 26 54 00 – Classified Location Lighting

GENERAL

SCOPE

Furnishing, installation, and assembly of lighting fixtures for areas classified as hazardous.

REFERENCES

National Fire Protection Association (NFPA):

NFPA 70	National Electrical Code (NEC)

CSA Group

Canadian Electrical Code (CEC)

CSA C22.2 No. 137  Luminaires for use in Hazardous (Classified) Locations

Underwriters Laboratories, Inc. (UL):

UL844	Luminaires for use in Hazardous (Classified) Locations

UL1598	Luminaires

UL1598A	Supplemental Requirements for Luminaires for Installation on Marine Vessels

UL8750	Light Emitting Diode (LED) Equipment for Use in Lighting Products

UL50	Enclosures for Electrical Equipment, Non-Environmental Considerations

UL50E	Enclosures for Electrical Equipment, Environmental Considerations

National Electrical Manufacturers Association (NEMA)

SUBMITTALS - FOR REVIEW/APPROVAL

The following information shall be submitted to the engineer.

Manufacturer’s descriptive literature and technical specifications for each product

Manufacturer’s product drawing (2D or 3D), when requested

Manufacturer’s installation and maintenance document

QUALIFICATIONS

- The supplier of the assembly must be the manufacturer of the major components within the assembly.

- For the equipment specified herein, the manufacturer must be ISO 9001 certified.

- The manufacturer of this equipment must have produced similar electrical equipment for a minimum period of five (5) years.  When requested by the engineer, an acceptable list of installations with similar equipment will be provided demonstrating compliance with this requirement.

- Products must be free of defects in material and workmanship

REGULATORY REQUIREMENTS

- The luminaire shall meet the following certifications:

  - NEC and CEC

      - Class I, Division 1, Groups C, D

      - Class II, Division 1, Groups E, F, G

      - Simultaneous Presence

      - NEMA 4X, IP66

      - Marine and Wet Location Rated

  - UL Standards

      - UL844

      - UL1598 Luminaires

      - UL1598A Marine

  - CSA Standard

      - cUL Listed to CSA Standard CSA C22.2 No. 137

DELIVERY, STORAGE, AND HANDLING

Store products in manufacturer’s unopened packaging until ready for installation

PRODUCTS

MANUFACTURERS

Acceptable Manufacturers:

Eaton’s Crouse-Hinds Business

1201 Wolf Street

Syracuse, NY 13208

(866) 764-5454

www.crouse-hinds.com

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features, and functions.  Manufacturers listed above are not relieved from meeting these specifications in their entirety.  Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the engineer ten (10) days prior to bid date.

ELECTRICAL REQUIREMENTS

Standard input driver voltage of 100-277 VAC, 50/60 Hz with optional drivers having 347-480 VAC.

Power factor >0.95 @ 277 VAC and THD <20% @ 277 VAC.

DC input of 108-250 in addition to above mentioned 100-277 VAC input must be available on a single driver.

System efficiency: minimum of 115 lumens per watt (LPW) for standard glass lens 4ft 100-277 VAC fixtures.

LED fixtures will include 2 or 3 pole terminal blocks with clearly marked input/output for line, neutral and ground electrical connections.

Drivers must have an L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e. no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range).

The drivers will have inbuilt 0-10V dimming function and capable of being wired to an external occupancy sensing/dimming device using two dimming leads.

External surge protection option for up to 10kV must be provided as a component within the complete luminaire.

Maximum desired input power (wattage) and current (amps) by fixture type @ 100 VAC and 277 AC:

| Lumen Levels (Typical) | Wattage @ 100 VAC | Amperes @ 100 VAC | Wattage @ 277 VAC | Amperes @ 277 VAC |
| --- | --- | --- | --- | --- |
| 7600 | 63.0 | 0.63 | 63 | 0.23 |
| 3800 | 33.0 | 0.33 | 34 | 0.14 |

material requirements

LED housing assembly and heat sink must be of extruded aluminum with low copper content for corrosion protection and heat dissipation.

LED board assembly lens cover must be made of heat and impact resistant glass. Diffused options need to be available for glass.

Fixture must utilize nitrile type gaskets between the driver and LED housing as well as the lens cover and LED board for ingress protection against dust and water.

Fixtures must not contain mercury or any other hazardous chemicals.

Diffused lens options for glass must be available for applications requiring low glare.

Fixture shall have external surface of low copper aluminum and nitrile type gaskets between the lens and LED board assembly, driver and LED housing for protection against acids (including acetic acid), sulfur, water (liquid and vapor form), hydrocarbons, and chlorine.

design and performance requirements

Overall height of fixture without mounting brackets must not exceed 4.8” and with mounting brackets must not exceed 8”.

The fixture must have 4 points of secondary retention integrated into the fixture for attaching safety cables.

The fixture design must have serviceable drivers accessible from the bottom of fixture and field replaceable without removing the fixture from a ceiling or wall mount installation.

The power supply or driver must be located in line with LED boards and not on top of them to maximize thermal dissipation and maintain lower driver baseplate temperatures

2 pole or 3 pole lever lock Wago connectors must be utilized for wiring connection from LEDs to drivers and from drivers to supply mains.

Fixture must be high pressure hose tested at 3 gallons per minute, 2000 psi@ 5ft distance with a 1/16” nozzle for 30 minutes to prevent ingress due to high pressure hosing.

Thermal pad must be utilized instead of thermal grease for heat dissipation from PCB board.

Reflectors must be utilized to obtain wide (120 deg) optical patterns.

Drivers must have a L10 reliability of a minimum of 60,000 hours @ 55°C ambient (i.e. no more than 10% of drivers installed in the field may fail catastrophically in the above specified duration and temperature range).

Fixtures must have a start-up and operating ambient temperature range of -25°C to +65ºC.

Water must not enter the compartment that houses wiring, wiring devices, or lamps under any condition of exposure other than submersion.

Fixtures must have Design Lights Consortium® approval and listing for cool white low voltage (100-277 VAC), high voltage (347-480 VAC), glass lens and standard wide optic.

Fixture must successfully be tested for 3 axis (5G) vibration @ 30 Hz frequency using all mounting options to withstand extreme vibration-prone environments.

Fixtures will have the following T-codes or higher various voltages and ambient temperatures.

| Ambient Temp | Min Supply Wire Temp | Class I, Division 1 | Class II, Division 1 | Simultaneous Presence | Paint Spray Applications |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Class I, Division 2 and Class II, Division 1 |  |
| 40°C | 75°C | T6 | T6 | T6 | T5 |
| 55°C | 75°C | T5 | T5 | T5 | T5 |
| 65°C | 90°C | T5 | T5 | T4A | T5 |

led system and optics requirements

LED fixtures must have correlated color temperature of 5000K with a 5 step Macadam ellipse tolerance.

Fixtures must use discrete Luxeon Tx power emitters with a minimum CRI of 70 @ 5000K and L70 > 400,000 @ 65°C ambient.

LED fixtures must have a rated life of a minimum 60,000 hours @ operating ambient temperature of 55°C.  This must be a complete system life including life of drivers.

The fixture shall have standard wide (120 degree) optic.

Fixtures should have a minimum efficacy of 115 lumens/watt @ 100-277 VAC

The following lens options must be available with LED light fixture:

            - Clear glass

            - Diffused glass (non-glare)

The fixture must have following typical lumen output ratings for cool white color, glass lens, and standard wide optic.

| System Configuration | Nominal Lumen Output @ 25°C (+/- 10% tolerance) |
| --- | --- |
| 4ft Linear | 7600 |
| 2ft Linear | 3800 |

The lumen, efficacy, wattage, CRI, CCT, power factor, THD, amperage, insitu temperature data, and L70 lifetime must be validated from third party LM79, LM80, and TM21 calculation reports.

EXECUTION

INSTALLATION

The fixture must have a back flange with sliding ceiling, swivel and flush mount bracket options to adjust the distance between two brackets and allow for flexible installation

The fixture should also have pole mount options.

3-conductor wiring should be looped inside ¾” side entry to allow easy wiring in a conduit or cable using 2 pole or 3 pole Wago lever lock conductors.

Loop feed access must be factory installed for feeding cable inside the fixture

Safety cables with locking carabineers must be available for secondary retention