GuideLed 10825 1-8h/D CGLine+ for wire suspension with canopy

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm and canopy with height of only 33mm.

Wire mounting set includes transparent insulated wire suspension for voltage supply.

Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N

at the end of the rated service time:		single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				20 m

Housing material: 				PC, PMMA

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				II (protective earth required)

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134, D = 12

Dimensions of ceiling mounting set (mm):	W = 226, H = 33, D = 80

3rd party certificate:				ENEC

Type: GuideLed 10825 1-8h/D CGLine+ for wire suspension with canopy

Manufacturer: CEAG

GuideLed  10826 1-8h/D CGLine+  for wire suspension and ceiling recessing of supply device

Pos.    )		ea.

Self-monitoring LED self-contained escape sign luminaire for wire suspension according to DIN EN 60598-1, DIN EN 60598-2-22 and DIN EN 1838 for systems according to DIN EN 50172, DIN VDE 0100-560 and DIN V VDE V 0108-100 for separate operation or for connection to the central monitoring facility CGLine+ Web-Controller (requires a non-shielded 2-core bus line).

Escape sign with LED Lightguide technology for especially homogeneous and

bright illumination of the pictogram acc. DIN 4844-1 and ISO 3864-1:

Lm >= 500 cd/m² (mains operation) for the white contrast colour and

Lm >= 200 cd/m² (mains operation) over the complete pictogram; uniformity Lmin/Lmax > 0.8.

LED-strip with high service life via optimised LED operating conditions and high luminous efficacy >100 lm/W for significantly reduced connected load. Easy connection via polarity reversal-protected wiring.

Slender design with low pictogram width of only 12mm. Freely settable suspension height adjusted without tools via steel cord holders to 1.5 m, and freely positionable housing in the ceiling for LED converter, with cable strain relief on primary and secondary side.

Serial functionality:

- Emergency light operating duration settable at 1 h, 3 h or 8 h

- Dimmable in three steps (100%, 30%, 10%) with mains operation for use in dark ambient conditions

- Manual function test or duration test via testing button

- Test results with fault analysis (light sources, charging and battery circuit) and status displays

(Operation, function test, duration test) via 2-colour LED

- Automatic function test (weekly) and automatic duration test (every 6 months)

- Automatic charge monitoring and total discharge protection with switching lock

- No-load and short circuit monitoring

- 1 Minute switch-back delay to normal operation after mains return

- Blocking function via CGLine+ Web-Controller during idle operating times

- Generally suitable for maintained or non-maintained operation

Luminous flux E/N

at the end of the rated service time:		single-sided: 100% at 1 h, 80% at 3 h, 25% at 8h

double-sided: 100% at 1 h, 50% at 3 h, 15% at 8h

Battery						LiIon 3.7V 2000 mAh

Viewing distance: 				20 m

Housing material: 				PC, PMMA, sheet steel

Housing colour: 				light grey RAL 7035

Connection terminals:				Through-wiring from mains L, L’, N, PE to 2.5 mm²

CGLine+ bus through-wiring to 1.5 mm²

Connection voltage:				220 - 240 V AC, 50/60 Hz

Connected load with mains operation:		single-sided 4.8 VA / 4.1 W

double-sided 5.6 VA / 5.1 W

Insulation class: 				I

Protection rating: 				IP 40

Permissible ambient temperature: 		-5°C to +30°C (maintained mode)

0°C to +35°C (non-maintained mode)

Dimensions of LED pictogram (mm):		W = 226, H = 134, D = 12

Dimensions of module housing (mm):	  	W= 340, W = 50, H = 46  (angular construction)

3rd party certificate:				ENEC

Type: GuideLed 10826 1-8h/D CGLine+ for wire suspension and ceiling recessing of supply device

Manufacturer: CEAG